## Slide 1: Emerging Issues
David Gustafson
gusta002@umn.edu

## Slide 2: Industry Goals
Longterm
Treatment
Affordable

## Slide 3: What are the Issues
Treatment concerns
System operation
System care
Industry Changes

## Slide 4: Climate Change
Heavier rains
Warmer temperatures
Higher Groundwater levels
  Greater variation
Treatment concern

## Slide 5: Electrochemical Assisted Anaerobic Digestion
Power
Power supply
Electrodes
Biogas

## Slide 6: Experimental set-up
20 Liter reactor of the modified septic tank with electrodes
Schematics including electrodes position and connections
Photograph of empty reactor
Reactor treating wastewater
The effect of increasing the Eap to 0.6 V and 0.7 V is being evaluated

## Slide 7: Limiting Conditions
Saturated Soils
Bedrock
  Sandy soils
  Rocky Soils

## Slide 8
$10
Onsite Sewage Treatment Program
University of Minnesota
More than 50% 2mm or greater = bedrock
~A very thin wedding band is 2 mm

## Slide 9: Saturated vs Unsaturated Flow
Unsaturated for treatment
  LTAR
  SAR
Saturated for speed
  Hydraulic conductivity
Perc test or Soil Characteristics
BOTH

## Slide 10: Surface water Protection
Surface discharge
Prescription drugs
Grit
Treatment concern

## Slide 11: Ground water protection
Water treatment
  RO
  Iron filters
  Softeners
System Compliance
Treatment concern

## Slide 12: Water Conditioning
Softeners
Iron filters
RO Units

## Slide 13: Early Research
Septic Tank/Water Softener “Potential Effects of Water Softener Use on Septic Tanks Soil Absorption On-Site Wastewater Systems”
  University of Wisconsin-Madison
“The Effect of Home Water Softener Waste Regeneration Brines on Individual Aerobic Wastewater Treatment Plants”
  NSF International
Notes: The University of Wisconsin study was conducted to test the hypothesis that if softener discharge harms a septic tank’s performance it would show up in the septic tank effluent clogging the soil systems or otherwise interfering with its performance.
The NSF study was conducted to measure the impact of salt from water softener discharge on biological action in the septic system, and to determine if the volume and flow rate of the discharge could overwhelm septic systems

## Slide 14: Recent Studies
Novak et. al, VA Tech findings in regard to Industrial Aerobic Activated Sludge systems:
  An imbalance in the monovalent to divalent (M/D) cation ratio can lead to poor settling
  This had not been tested in anaerobic systems.
    Poor settling and lack of clear zones may be due to excessive sodium (M) in relation to calcium (D) and magnesium (D).
Notes: Note to self: Novak presented his work at the WERF workshop.

## Slide 15: Study Goals
Illustration from www.genie.com
Look at amount and capture of suspended solids
Look at ability to separate layers and quality of effluent
Notes: Will apply to advanced treatment systems, too, because primary treatment is anaerobic with secondary treatment being aerobic for polishing or further treatment of the waste water.

## Slide 16: Outcomes
More research
Choosing “Better Units”
  No Brine
  Flow based
  Time based – Potential issues
Softener Care
Be careful with Advanced technologies

## Slide 17: System Specifics
Design & Layout
Special wastes
  HSW
  Hard to treat

## Slide 18
Closed restaurant [Really Famous Dave’s ~ 20 seats and 15 seats in bar] wants to reopen and add patio seating [22 more seats]
System Loading

## Slide 19: Design Confusion
Residential
  Assume BOD, TSS Loading
  Estimated use [Bedrooms]
Non-Residential
  Higher Organic loading
Care facilities
VRBO
THE CODE

## Slide 20: Flow Changes
Check “Old Design”
New Numbers
20 Seats [Food] x 30 gpd
15 Seats [Bar] x 36 gpd
22 Seats [Patio] x [30-36] gpd
11 Employees x 15 gpd
600 gpd
540 gpd
660-792 gpd
165 gpd
1,965-2,097 gpd
2,000 gpd

## Slide 21: Tank Sizing
Remember “Grease trap”
Typically 1 times the Kitchen flow
  70% total flow
  2,000 x 70% =
Septic tank: 3 x Design flow
  2,000 gpd x 3 days =
  Or 4 times and skip grease trap
1,400 gal
6,000 gal
8,000 gal

## Slide 22: System Sizing
After service check STA loading
Measured flow ~ 890 gpd
Measured BOD5 ~ 755 mg/L
# BOD5 = Flow x Conc. X 8.35÷1,000,000
890 gpd x 755 mg/L x 8.35÷1,000,000
5.6 lbs

## Slide 23: Soil Organic Loading Rate
SOLR = # ÷ Sqft
5.6 # ÷ 2,000 Sqft
3,333 sqft
2,000 sqft
Table 5.1 SOLR—Bottom Area Only |  |  | 
SHLR | lbs of BOD/ ft2/day of total absorption area | lbs of TSS/ft2/day of total absorption area | lbs of FOG/ft2/day of total absorption area
Sand [1.2] | 0.0017 | 0.0006 | 0.0003
Sandy Loam [0.78] | 0.0011 | 0.0004 | 0.0002
FS, Loam [0.6] | 0.0009 | 0.0003 | 0.0001
Silt Loam [0.5] | 0.0007 | 0.0003 | 0.0001
Clay Loam [0.45] | 0.0006 | 0.0002 | 0.0001
0.003
0.002
Too High
Too High

## Slide 24: Solutions
More Area
# of BOD5 ÷ SOLR
5.6 ÷ 0.0009 #/sqft=
Pretreatment
6,222 sqft

## Slide 25: Sizing Issues~ Solutions
Backward Design
  Area Limited
  Contour Limited
  Treatable Design flow
    Flow equalization

## Slide 26: CLR Example~ Good Site
Good site with only a 40’ contour available
Recommended CLR = 12 gpd/ft
Design flow = Contour length x CLR
Design flow = 40 ft x 12 gpd/ft
Timer setting = 70% of Design flow
Timer setting = gpd x .7 [70%]
480 gpd
336 gpd

## Slide 27: Example~ Ugly Site
Ugly site with only a 40’ contour available
Recommended CLR = 6 gpd/ft
Design flow = Contour length x CLR
Design flow = 40 ft x 6 gpd/ft
Timer setting = 70% of Design flow
Timer setting = gpd x .7 [70%]
Perc rate 133 mpi
240 gpd
170 gpd

## Slide 28: Example: Limited width
5 Bedroom Type I home
Site with Clay [88 mpi] and an available area of 35’ x 40’ on the site
35’
40’
3%

## Slide 29: Clay [88 mpi]
MAR~
CLR = Width ÷ MAR
CLR = 40’ ÷ 5
System Max Flow = Length x CLR
System Max Flow = 35’ x 8 gpft
Timer Setting = 70% of Max flow
Timer Setting = gpd x .7
5
8 gpft
280 gpd
196 gpd

## Slide 30: The Industry
Unknowns
  MRSA Bacteria
Current practices
  Land Application
Business Transition
  Work force age

## Slide 31: Safety
OSHA
  Excavation focus
Pathogens
MRSA
  Methicillin-resistant Staphylococcus aureus
  Anti-biotic Resistant

## Slide 32: Today’s Regulations
Relationships
Understanding
  Two Parties
Moving forward
MN example

## Slide 33: Questions